## Table 1
IDENTIFICATION | AREA SERVED | MANUFACTURER | MODEL NUMBER | NOMINAL TONS | UNIT TYPE | UNIT EER | SEER /IEER | SUPPLY FAN | [8 empty] | COOLING COIL |  |  |  | HEATING COIL | [5 empty] | CONDENSER |  | RELIEF FAN | [5 empty] | REFRIGERANT |  | UNIT ELECTRICAL |  |  | FILTER TYPE | OPERATING WEIGHT (LBS) | REMARKS
[8 empty] | CFM | OUTSIDE AIR |  | ESP (IN. WG) | TSP (IN. WG) | QTY | BHP (EA) | HP (EA) | RPM | EAT DB/WB (° F) | LAT DB/WB (° F) | SENSIBLE CAPACITY (MBH) | TOTAL CAPACITY (MBH) | CFM | EAT (° F) | LAT (° F) | CAPACITY (MBTUH) | GAS CFH | AFUE | QTY FANS | HP (EA) | CFM | RETURN DUCT STATIC PRESSURE (IN. WG) | QTY | BHP | HP | RPM | TYPE | CHARGE CIRCUIT 1 / 2 (LBS) | VOLT/PH | MCA | MOCP
[9 empty] | MIN. | MAX.
RTU-1 | LEVEL 2 SPACES | TRANE | SAHPF6040 | 60 | MULTIZONE VAV | 11 | 18.4 | 17700 | 2500 | 17700 | 3.25 | 4.81 | 2 | 10.14 | 15 | 2000 | 75.2 / 63.8 | 50.6 / 50.5 | 465 | 661 | -- | -- | -- | -- | -- | -- | 6 | 1 | 15200 | 1 | 1 | 3.95 | 5 | 700 | R-454B | 41.0 / 38.5 | 460 / 3 | 155 | 175 | 2 | 10184 | A, B, C, E, F, H, I, K, L, M
RTU-2
RTU-3
RTU-4